## Vendor Scope
PIC OUTAGE MAINTENANCE ELECTRIC, INSTRUMENTATION & CONTROL
UNIT 1 2026
VENDOR SCOPE
Coordinator (Progress monitoring & Report) : | M Farhan / H Aidi
A. Peralatan Electric Utama dan Bantu | 2026 | SCOPE VENDOR | MSW PIC
1. Electric Generator 31,5 MW/11 kV | ME | Pengukuran tahanan isolasi, indeks polarisasi (PI), winding resistance test, connection check, pemeriksaan cooler, cek sistem excitasi, PMG, dan kebersihan saluran ventilasi, grounding check | M ZAINI
2. Generator Trafo 40 MVA,11/66 kV | ME | Pengujian tahanan isolasi, uji tegangan tembus, dan pembersihan bushing, pengencangan baut, dan pengujian fungsi proteksi, cek BDV oli trafo, grounding check | M ZAINI
3. MV Auxiliary Trafo 10 MVA,11/6.6 kV | ME | Pengujian tahanan isolasi, uji tegangan tembus, dan pembersihan bushing, pengencangan baut, dan pengujian fungsi proteksi, cek BDV oli trafo, grounding check | M ZAINI
4. LV Auxiliary Trafo 2.5 MVA,6.6/0.4 kV | ME | Pengujian tahanan isolasi, uji tegangan tembus, dan pembersihan bushing, pengencangan baut, dan pengujian fungsi proteksi, cek BDV oli trafo, grounding check | M ZAINI
5. ESP Rectifier Trafo 250 kW,380 VAC/70 kVDC | ME | Pengujian tahanan isolasi, uji tegangan tembus, dan pembersihan bushing, pengencangan baut, dan pengujian fungsi proteksi, cek BDV oli trafo, grounding check | M IQBAL
6. Panel MV Switchgear 6.6 kV | ME | Uji contact resistance pada CB, uji timing close-open, dan pelumasan mekanisme mekanis CB, grounding check | M ZAINI
7. Panel LV PMCC 380 V | ME | Uji contact resistance pada CB, uji timing close-open, dan pelumasan mekanisme mekanis CB, grounding check | M ZAINI
8.Panel MCC 380 V (Boiler,Turbin Generator, ESP,AHP) | ME | Uji contact resistance pada CB, uji timing close-open, dan pelumasan mekanisme mekanis CB, grounding check | M ZAINI
9. Panel Generator CB | ME | Uji contact resistance pada CB, uji timing close-open, dan pelumasan mekanisme mekanis CB, grounding check | M ZAINI
Panel Generator CB 11 ME Penggantian Voltage Transformer | ME |  | H AIDI
10. Generator Control Panel | ME |  | M ZAINI
11. Generator Exciter Panel | ME |  | M ZAINI
12. Panel Bapcon – Rapcon ESP | ME |  | M IQBAL
13. Panel Inverter LV motor | ME |  | M ZAINI
14. Panel Soft Starter/FCMA | ME |  | H AIDI
15. Relay Proteksi | ME | Pengujian injeksi sekunder (Secondary Injection Test) untuk memastikan relay trip sesuai kurva waktu dan nilai arus settingnya, cek log kejadian (event recorder) | M ZAINI
16. LV Motor 380 V | SI | Pengukuran tahanan isolasi, indeks polarisasi (PI), connection check, cek visual body, fan cover, dan kebersihan saluran ventilasi | YOGA
17. MV Motor 6.6 kV | ME | Pengukuran tahanan isolasi, indeks polarisasi (PI), connection check, cek visual body, fan cover, dan kebersihan saluran ventilasi | H AIDI
BFP motor 2 Perbaikan leak oil bearing sisi NDE | ME |  | YOGA
18. HV Apparatus Bay Trafo 66 kV (T&D) | ME |  | T&D
19. HV Apparatus Bay Coupler (T&D) | ME |  | T&D
20 Marshaling Kiosk | ME |  | T&D
21. Remote Control Panel (RCP) | ME |  | M ZAINI
22. Busduct Trafo | SI | Pengujian tahanan isolasi, kontak resistan bagian konduktor, grounding check | M IQBAL
23. Busduct Generator | SI | Pengujian tahanan isolasi, kontak resistan bagian konduktor, grounding check | M IQBAL
24. MV Motor Cable 6.6 kV | SI | Pengukuran tahanan isolasi, indeks polarisasi (PI), connection check, cek visual body, fan cover, dan kebersihan saluran ventilasi | M IQBAL
25. LV Motor Cable 380 V | SI | Pengukuran tahanan isolasi, indeks polarisasi (PI), connection check, cek visual body, fan cover, dan kebersihan saluran ventilasi | M IQBAL
26. Electrical Grounding | SI | Visual Inspection pada sambungan dan kerusakan, tightening & cleaning, pengukuran grounding resistance dan verifikasi | YOGA
B. Instrument
1. Panel DCS | SI | Cek kondisi fisik panel (kebersihan, pintu, kunci, dan grounding), indikator LED CPU/I/O/Power Supply, suhu panel, serta memastikan tidak ada alarm atau fault aktif di sistem. | JHON
2. Pressure tx range -70~1500 mBar | SI | Verifikasi Dan Kalibrasi | FERRYUS
3. Pressure tx range -1~180 Bar | SI | Verifikasi Dan Kalibrasi | FERRYUS
4. Flow tx range -500~12500 mmH2O | SI | Verifikasi Dan Kalibrasi | FERRYUS
5. Temperature tx range 0 ~ 1200 celcius | SI | Verifikasi Dan Kalibrasi | FERRYUS
C. Rotating
Gland Steam Sealing Condenser | ME | Pengukuran tahanan isolasi, indeks polarisasi (PI), connection check, cek visual body, fan cover, dan cek tightening terminal kabel. | H AIDI
Rotary coal Feeder 1 | SE | Replace Motor & Gear box | H AIDI
Rotary coal Feeder 2 | SE | Replace Motor & Gear box | H AIDI
D. Actuator Valve
KSB MIL SPRAY WATER LINE CONTROL VALVE, FEED WATER 30% | ME | GENERAL INSPECTION | M TOHER
KSB MIL SPRAY WATER LINE CONTROL VALVE, FEED WATER 100% | ME | GENERAL INSPECTION | M TOHER
KSB MIL SPRAY WATER LINE CONTROL VALVE, DESUPERHEATER 1&2 | ME | GENERAL INSPECTION | M TOHER
KSB MIL SPRAY WATER LINE CONTROL VALVE, DESUPERHEATER 1&2 | ME | GENERAL INSPECTION | M TOHER
Deaerator KSB MOV Gate Valve 1-1/2'' | ME | GENERAL INSPECTION | M TOHER
Deaerator KSB MOV 2'' | ME | GENERAL INSPECTION | M TOHER
Forbes Marshall WCV PRDS CONTROL VALVE | ME | GENERAL INSPECTION | M TOHER
Forbes Marshall PRDS CONTROL VALVE | ME | GENERAL INSPECTION | M TOHER
MFT Boiler Coal Gate | ME | GENERAL INSPECTION, Add modify chute drain with Isolation Valve | M TOHER
ID Fan Inlet Gate Valve (Valve+Penumatic Actuator) IGV | ME | GENERAL INSPECTION | M TOHER
ID Fan Inlet Damper (Valve+Motorized) | ME | GENERAL INSPECTION, Replace MOV | M TOHER
ID Fan Outlet Damper (Valve+Motorized) | ME | GENERAL INSPECTION | M TOHER
HP BYPASS Control Valve (Valve+Actuator) | ME | GENERAL INSPECTION | M TOHER
E. Turbine Major Outage
Instrument | SE | Verifikasi Dan Kalibrasi | FERRYUS/JHON
Generator Bearing | SE | Replace Motor & Gear box | H AIDI
SI: Inspection
ME: Minor
SE: Major

## MSW SCOPE
PIC OUTAGE MAINTENANCE ELECTRIC, INSTRUMENTATION & CONTROL
UNIT 1 2026
MSW SCOPE
MSW SCOPE | Activity | MSW PIC
Unit 1 - GCB Panel Cooling Fan Blower rusak Mx | Replace | M ZAINI
PRESSURE SWITCH | Verifikasi & Calibrasi | FERRYUS
ACTUATOR ON OFF VALVE | General Inspection | JHON
IGV CONTROL (SA, SUB) | General Inspection | JHON
GOVERNOR VALVE | General Inspection | JHON
ACTUATOR CONTROL VALVE | General Inspection | M TOHER
ACTUATOR MOTORIZED VALVE | General Inspection | M TOHER
PROTECTION TEST | Function test | JHON
LEVEL SWITCH | Verifikasi & Function Test | FERRYUS
FIRE ALARM SYSTEM | Verifikasi & Function Test | M TOHER