## Actuator Valve
PROGRESS OM ACTUATOR VALVE UNIT 2
|  | FINISH | IN PROGRESS | TOTAL | % IN PROGRESS | % FINISH
|  | 92 | 0 | 92 | 0 | 100
AREA | DESCRIPTION | FINISH DATE | PIC | PROGRESS | % | REMARKS
BOILER | ACTUATOR FEED WATER CONTROL VALVE 100% 20LAB30AA220 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | ACTUATOR FEED WATER CONTROL VALVE 30% 20LAB30AA210 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | ACTUATOR DESH-1 SPRAY WATER ISOLATION |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | ACTUATOR DESH-1 SPRAY WATER CONTROL VALVE |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | ACTUATOR DESH-2 SPRAY WATER ISOLATION |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | ACTUATOR DESH-2 SPRAY WATER CONTROL VALVE |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | ACTUATOR FUEL COAL GATE VALVE 1 (MFT-1) 20HHE11AA01 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | ACTUATOR FUEL COAL GATE VALVE 2 (MFT-2) 20HHE12AA01 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
ID FAN | ACTUATOR IGV ID FAN 1 20HNC01EX001 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
ID FAN | ACTUATOR IGV ID FAN 2 20HNC01EX002 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
ID FAN | ACTUATOR INLET ID FAN 1 MOV 20HNA61AA001 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
ID FAN | ACTUATOR INLET ID FAN 2 MOV 20HNA62AA001 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
ID FAN | ACTUATOR OUTLET ID FAN 1 MOV 20HNA71AA001 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
ID FAN | ACTUATOR OUTLET ID FAN 2 MOV 20HNA72AA001 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
PA FAN | ACTUATOR MOV OUTLET PA FAN 1 |  | AMP | FINISH | 100
| General Inspection, Calibration and Cleaning |  | AMP |  | TRUE
| Function Test |  | AMP |  | TRUE
PA FAN | ACTUATOR MOV PA FAN 1 |  | AMP | FINISH | 100
| General Inspection, Calibration and Cleaning |  | AMP |  | TRUE
| Function Test |  | AMP |  | TRUE
STG | BFP SPRAY LINE (FEED WATER) TO DEAERATOR PRDS I/L MOV 20LAE10AA110 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
STG | ACTUATOR MAIN STEAM LINE (START UP BYPASS) TO DEAERATOR PRDS I/L CV 20LBH10AA210 |  | AMP | FINISH | 100 | Spring Patah
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
STG | ACTUATOR BFP SPRAY LINE (FEED WATER) TO DEAERATOR PRDS I/L CV 20LAE10AA210 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
STG | ACTUATOR TURBINE EXTRACTION III TO DEAERATOR CV 20LBD20AA210 |  | AMP | FINISH | 100 | Seat Valvenya terangkat tdk duduk di body valvenya sehingga menghalangi pergerakan stem menuju close. Yg mmbuat seat valve terangkat krna threadnya loss/dol.
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
STG | MOV DISCHARGE BFP-1 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
STG | MOV DISCHARGE BFP-2 |  | AMP | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | ACTUATOR ISOLATION STARTUP VENTING BOILER |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | ACTUATOR IGV SA FAN 1 20HLB01EX001 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-21 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | ACTUATOR IGV SA FAN 2 20HLB02EX001 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-21 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | ACTUATOR IGV SA CONTROL DAMPER 20HLA25AA010 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-22 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | ACTUATOR IGV SUB 1 20HJL10AA010 |  | MSW | FINISH | 100 | ada kebocoran pada shaft silinder sehingga mempengaruhi pada saat Open
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-22 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | ACTUATOR IGV SUB 2 20HJL11AA010 |  | MSW | FINISH | 100 | Shaft silinder berat pada saat start open dari 0%-25%
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | ACTUATOR BED MATERIAL DISCHARGE GATE VALVE 20ETG31AA01 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-22 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | ACTUATOR VALVE DRAIN SOOT BLOWER 20HCB10AA201 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | COMBUSTER ASH DRAIN 1 (BED ASH COLLER DRAIN) MOV 20HHC01AA001 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | COMBUSTER ASH DRAIN 2 (EMERGENCY ASH DRAIN) MOV 20HHC01AA002 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
BOILER | SOOT BLOWER CONTROL VALVE |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | SOOT BLOWER ISOLATION VALVE MOV 20HCB10AA001 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | MS START UP VENT VALVE (REG) MOV 20LBA21AA011 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | MS START UP VENT VALVE (ISO) MOV 20LBA21AA001 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | ACTUATOR SOOT BLOWER CV 20HCB10EX001 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
BOILER | ACTUATOR DAMPER SEALPOT BLOWER 1 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
BOILER | ACTUATOR DAMPER SEALPOT BLOWER 2 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
BOILER | COMBUSTER ASH DRAIN 1 (BED ASH COLLER DRAIN) MOV 10HHC01AA001 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | COMBUSTER ASH DRAIN 2 (EMERGENCY ASH DRAIN) MOV 10HHC01AA002 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
BOILER | FLUIDIZING VALVE BED MATERIAL |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
BOILER | FLUIDIZING VALVE LIMESTONE 1&2 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
DRUM | ACTUATOR STEAM DRUM VENTING ISOLATION VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
DRUM | ACTUATOR STEAM DRUM MOV VENTING VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
DRUM | ACTUATOR STEAM DRUM CBD ISOLATION VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
DRUM | ACTUATOR STEAM DRUM MOV CBD CONTROL VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
DRUM | ACTUATOR STEAM DRUM IBD ISOLATION VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
DRUM | ACTUATOR STEAM DRUM MOV IBD CONTROL VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
PA FAN | ACTUATOR MOV OUTLET PA FAN 2 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
PA FAN | ACTUATOR MOV PA FAN2 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SA FAN | ACTUATOR MOV OUTLET SA FAN 1 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SA FAN | ACTUATOR MOV OUTLET SA FAN 2 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
STG | ACTUATOR HP BYPASS CONTROL VALVE 20LBF10AA210 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
STG | ACTUATOR CONDENSATE PUMP RECIRCULATION CONTROL VALVE 20LCA31AA210 |  | MSW | FINISH | 100 | Ada kebocoran pada Seal Shaft & Air lock relay
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | ACTUATOR MAIN CONDENSATE CONTROL VALVE 20LCA30AA240 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | ACTUATOR GLAND STEAM PRESSURE CONTROL VALVE 20MAW10AA210 |  | MSW | FINISH | 100 | Pada Seal shaft juga ditemukan kebocoran-->Belum bisa diaction
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE | -Function Test --> Valve sangat Hunting-->Auto Calibration, Adjust Deadband & tuning manual KP (Proportional Gain)-->Function Test after Cal
| FUNCTION TEST |  | MSW |  | TRUE
STG | ACTUATOR GLAND STEAM TEMP. CONTROL VALVE 20LCE10AA210 |  | MSW | FINISH | 100 | -Diagfram, york & accesories tdk ada kebocoran, Connector ada beberapa yg bocor-->Resealing (OK).
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE | -Function Test --> Valve Hunting-->Auto Calibration & Adjust Deadband-->Function Test after Cal
| FUNCTION TEST |  | AMP |  | TRUE
STG | ACTUATOR BYPASS SPRAY CONTROL VALVE 20LCE40AA210 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | AMP |  | TRUE
| FUNCTION TEST |  | AMP |  | TRUE
STG | CEP DISCHARGE VALVE |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-20 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | DISCHARGE, SUCTION & VENTING VALVE VACUM PUMP-1 & 2 |  | MSW | FINISH | 100 | discharge valve Vacum Pump-1 bocor di SV, cover SV-nya retak.
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-20 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | MOV MAIN STEAM DRAIN STG-2 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | DRAIN OF ESV 20MAL10AA210 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-20 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | DRAIN OF CV CHAMBER 20MAL20AA210 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-20 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | TURBINE DRAIN VALVE AFTER FIRST STAGE 20MAL30AA210 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-20 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | TURBINE DRAIN VALVE 20MAL40AA210 |  | MSW | FINISH | 100 | Air Regulator Valve no. 4 sdh diganti baru.
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-20 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | TURBINE DRAIN VALVE 20MAL50AA210 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-20 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | TURBINE DRAIN VALVE 20MAL60AA210 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning | 2026-07-20 | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
STG | TURBINE DRAIN VALVE 20MAL70AA210 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning | 2026-07-20 | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
STG | CONTROL VALVE LPH-2 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | CONTROL VALVE LPH-1 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | MOV TURBINE STEAM EXTRACTION-1 & 2 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING | 2026-07-21 | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
STG | ACTUATOR MOV TURBINE STOP VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
STG | ACTUATOR MOV PREHEATING 1 TURBINE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
STG | ACTUATOR MOV PREHEATING 2 TURBINE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
STG | ACTUATOR ON/OFF NRV STEAM EXTRACTION 1, 2, 3 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
STG | ACTUATOR ON/OFF VALVE CEP-1 & CEP-2 |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning | 2026-07-20 | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SUB BURNER 1 VALVE 20HJN11AA003 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
SUB | ACTUATOR SUB BURNER 2 VALVE 20HJN12AA003 |  | MSW | FINISH | 100
| GENERAL INSPECTION, CALIBRATION AND CLEANING |  | MSW |  | TRUE
| FUNCTION TEST |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER MAIN LDO LINE CONTROL VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 1 LDO LINE CONTROL VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 1 ATOMISING AIR LINE CONTROL VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 2 LDO LINE CONTROL VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 2 ATOMISING AIR LINE CONTROL VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 1 ATOM AIR ISOLATION VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 1 LDO ISOLATION VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 1 SCAVENGING VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 2 ATOM AIR ISOLATION VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 2 LDO ISOLATION VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
SUB | ACTUATOR SKID BURNER 2 SCAVENGING VALVE |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
BOILER | ACTUATOR MOV INLET ECONOMIZER |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
BOILER | ACTUATOR MOV RECIRCULATION ECONOMIZER |  | MSW | FINISH | 100
| General Inspection, Calibration and Cleaning |  | MSW |  | TRUE
| Function Test |  | MSW |  | TRUE
PT MAKMUR SEJAHTERA WISESA
2 X 30 MW COAL FIRED POWER PLANT
EIC SECTION